## Tech Spec-C
Technical specification : Seires name (Model range) R-410a 50Hz Rev.0
Item | Capacity |  | kW | 3.5 | 5 | 7 | 9 | 12 | 14
1 | Model name |  | Unit | WPC04D1D | WPC05D1D | WPC07D1D | WPC09D1D | WPC12D1D | WPC14D1D
2 | Power supply |  | V/Ph/Hz | 230- 240v/1/50 | 230- 240v/1/50 | 230- 240v/1/50 | 230- 240v/1/50 | 380- 4150v/3/50 | 380- 4150v/3/50
3 | Cooling | Capacity | KW | 3.6 | 5 | 7.2 | 9.5 | 12.3 | 14
4 |  | Sensible cooling capacity | KW | 2.9 | 3.7 | 5.61 | 7.2 | 9.48 | 11.8
5 |  | Power Input | KW | 1.02 | 1.24 | 2 | 2.58 | 3.02 | 3.95
6 |  | Rated current | A | 4.4 | 5.83 | 9.25 | 11.5 | 4.77 | 6.45
7 |  | EER | W/W | 3.53 | 4.03 | 3.6 | 3.68 | 4.07 | 3.4568
8 | Max. input consumption |  | KW | 1.4 | 2.4 | 2.66 | 4 | 4.2 | 5.7
9 | Max. current |  | A | 6 | 10 | 11.38 | 17.1 | 5.5 | 7.4
10 | Starting current |  | A | 20 | 28 | 30 | 40 | 16 | 22
11 | External static pressure at (Hi) |  | Pa | 50 | 60 | 100 | 120 | 120 | 150
12 | Indoor air flow (Hi) |  | m3/h | 700 | 1000 | 1360 | 1700 | 2300 | 2700
13 | Indoor noise level(Hi) |  | dB(A) | 42 | 44 | 45 | 47 | 50 | 52
14 | Net Dimension | W | mm | 1065 | 1065 | 1165 | 1165 | 1365 | 1365
15 |  | H | mm | 405 | 405 | 455 | 455 | 555 | 555
16 |  | D | mm | 480 | 480 | 620 | 620 | 670 | 670
17 | Weight | Net | kg | 70 | 86 | 97 | 115 | 148 | 155
18 |  | Gross | kg | 78 | 94 | 107 | 127 | 136 | 165
19 | Compressor | Type |  | Rotary | Rotary | Rotary | Rotary | scroll | scroll
20 |  | Quantity |  | 1 | 1 | 1 | 1 | 1 | 1
21 | Water flow (nomina1) |  | m3/h | 0.79 | 1.04 | 1.58 | 2.09 | 2.63 | 3.2
22 | Diameter of water in/out pipe |  |  | DN20 | DN20 | DN20 | DN20 | DN25 | DN25
23 | Diameter of drain pipe |  | inch | 3/4 | 3/4 | 3/4 | 3/4 | 3/4 | 3/4
24 | Refrigerant control |  |  | capillary | capillary | capillary | capillary | capillary | capillary
25 | Water coil pressure drop |  | kpa | 25 | 40 | 41 | 40 | 51 | 55
26 | Refrigerant | Type |  | R410a | R410a | R410a | R410a | R410a | R410a
27 |  | Charge | g | 830 | 990 | 1020 | 1300 | 2050 | 2300
Remark: The above design and specification are subject to change without prior notice for product improvement.
| Rating Conditions |  |  | Cooling
| Indoor Temperature |  |  | 27oC DB/19oC WB
| water inlet temperature |  |  | 30oC
| water outlet temperature |  |  | 35oC

## Tech Spec-H
Technical specification : Seires name (Model range) R-410a 50Hz Rev.0
Item | Capacity |  | kW | 3.5 | 5 | 7 | 9 | 12 | 14
1 | Model name |  | Unit | WPH04D1D | WPH05D1D | WPH07D1D | WPH09D1D | WPH12D1D | WPH14D1D
2 | Power supply |  | V/Ph/Hz | 230- 240v/1/50 | 230- 240v/1/50 | 230- 240v/1/50 | 230- 240v/1/50 | 380- 4150v/3/50 | 380- 4150v/3/50
3 | Cooling | Capacity | KW | 3.6 | 5 | 7.2 | 9.5 | 12.3 | 14
4 |  | Sensible cooling capacity | KW | 2.9 | 3.7 | 5.61 | 7.2 | 9.48 | 11.8
5 |  | Power Input | KW | 1.02 | 1.24 | 2 | 2.58 | 3.02 | 3.95
6 |  | Rated current | A | 4.4 | 5.83 | 9.25 | 11.5 | 4.77 | 6.45
7 |  | EER | W/W | 3.53 | 4.03 | 3.6 | 3.68 | 4.07 | 3.4568
8 | Heating | Capacity | KW | 3.82 | 5.7 | 7.89 | 10.2 | 12.7 | 15
9 |  | Input | KW | 1.07 | 1.4 | 2.2 | 2.65 | 3.28 | 4.14
10 |  | Rated current | A | 4.8 | 6.35 | 9.81 | 11.9 | 5.15 | 6.83
11 |  | COP | W/W | 3.57 | 4.07 | 3.59 | 3.85 | 3.87 | 3.62
12 | Max. input consumption |  | KW | 1.4 | 2.4 | 2.66 | 4 | 4.2 | 5.7
13 | Max. current |  | A | 6 | 10 | 11.38 | 17.1 | 5.5 | 7.4
14 | Starting current |  | A | 20 | 28 | 30 | 40 | 16 | 22
15 | External static pressure at (Hi) |  | Pa | 50 | 60 | 100 | 120 | 120 | 150
16 | Indoor air flow (Hi) |  | m3/h | 700 | 1000 | 1360 | 1700 | 2300 | 2700
17 | Indoor noise level(Hi) |  | dB(A) | 42 | 44 | 45 | 47 | 50 | 52
18 | Dimension | W | mm | 1065 | 1065 | 1165 | 1165 | 1365 | 1365
19 |  | H | mm | 405 | 405 | 455 | 455 | 555 | 555
20 |  | D | mm | 480 | 480 | 620 | 620 | 670 | 670
21 | Weight | Net | kg | 75 | 90 | 103 | 120 | 152 | 162
22 |  | Gross | kg | 82 | 97 | 110 | 129 | 161 | 170
23 | Compressor | Type |  | Rotary | Rotary | Rotary | Rotary | Scroll | Scroll
24 |  | Quantity |  | 1 | 1 | 1 | 1 | 1 | 1
25 | Water flow (nomina1) |  | m3/h | 0.79 | 1.04 | 1.58 | 2.09 | 2.63 | 3.2
26 | Diameter of water in/out pipe |  |  | DN20 | DN20 | DN20 | DN20 | DN25 | DN25
27 | Diameter of drain pipe |  | inch | 3/4 | 3/4 | 3/4 | 3/4 | 3/4 | 3/4
28 | Refrigerant control |  |  | capillary | capillary | capillary | capillary | capillary | capillary
29 | Water coil pressure drop |  | kpa | 25 | 40 | 41 | 40 | 51 | 55
30 | Refrigerant | Type |  | R410a | R410a | R410a | R410a | R410a | R410a
31 |  | Charge | g | 830 | 990 | 1020 | 1300 | 2050 | 2300
Remark: The above design and specification are subject to change without prior notice for product improvement.
| Rating Conditions |  |  | Cooling | Heating
| Indoor Temperature |  |  | 27oC DB/19oC WB | 20oC DB/15oC WB
| water inlet temperature |  |  | 30oC | 20oC
| water outlet temperature |  |  | 35oC | ----
850kg
2000

## Tech Spec-C+E
Technical specification : Seires name (Model range) R-410a 50Hz Rev.0
Item | Capacity |  | kW | 3.5 | 5 | 7 | 9 | 12 | 14
1 | Model name |  | Unit | WPC04D1DE | WPC05D1DE | WPC07D1DE | WPC09D1DE | WPC12D1DE | WPC14D1DE
2 | Power supply |  | V/Ph/Hz | 230- 240v/1/50 | 230- 240v/1/50 | 230- 240v/1/50 | 230- 240v/1/50 | 380- 4150v/3/50 | 380- 4150v/3/50
3 | Cooling | Capacity | KW | 3.6 | 5 | 7.2 | 9.5 | 12.3 | 14
4 |  | Sensible cooling capacity | KW | 2.9 | 3.7 | 5.61 | 7.2 | 9.48 | 11.8
5 |  | Power Input | KW | 1.02 | 1.24 | 2 | 2.58 | 3.02 | 3.95
6 |  | Rated current | A | 4.4 | 5.83 | 9.25 | 11.5 | 4.77 | 6.45
7 |  | EER | W/W | 3.53 | 4.03 | 3.6 | 3.68 | 4.07 | 3.4568
8 | Heating(Fan high speed) | Capacity | KW | 1.86 | 2.44 | 2.92 | 4.73 | 4.87 | 5.04
9 |  | Power Input（included fan） | KW | 1.9 | 2.52 | 3 | 4.81 | 4.97 | 5.12
10 |  | Rated current | A | 8.37 | 11.09 | 13.16 | 21.08 | 21.6 | 22.45
11 | Max. input consumption |  | KW | 1.4 | 2.4 | 2.66 | 4 | 4.2 | 5.7
12 | Max. current |  | A | 6 | 10 | 11.38 | 17.1 | 5.5 | 7.4
13 | Starting current |  | A | 20 | 28 | 30 | 40 | 16 | 22
14 | External static pressure at (Hi) |  | Pa | 50 | 60 | 100 | 120 | 120 | 150
15 | Indoor air flow (Hi) |  | m3/h | 700 | 1000 | 1360 | 1700 | 2300 | 2700
16 | Indoor noise level(Hi) |  | dB(A) | 42 | 44 | 45 | 47 | 50 | 52
17 | Net Dimension | W | mm | 1065 | 1065 | 1165 | 1165 | 1365 | 1365
18 |  | H | mm | 405 | 405 | 455 | 455 | 555 | 555
19 |  | D | mm | 480 | 480 | 620 | 620 | 670 | 670
20 | Weight | Net | kg | 70 | 86 | 97 | 115 | 148 | 155
21 |  | Gross | kg | 78 | 94 | 107 | 127 | 136 | 165
22 | Compressor | Type |  | Rotary | Rotary | Rotary | Rotary | scroll | scroll
23 |  | Quantity |  | 1 | 1 | 1 | 1 | 1 | 1
24 | Water flow (nomina1) |  | m3/h | 0.79 | 1.04 | 1.58 | 2.09 | 2.63 | 3.2
25 | Diameter of water in/out pipe |  |  | DN20 | DN20 | DN20 | DN20 | DN25 | DN25
26 | Diameter of drain pipe |  | inch | 3/4 | 3/4 | 3/4 | 3/4 | 3/4 | 3/4
27 | Refrigerant control |  |  | capillary | capillary | capillary | capillary | capillary | capillary
28 | Water coil pressure drop |  | kpa | 25 | 40 | 41 | 40 | 51 | 55
29 | Refrigerant | Type |  | R410a | R410a | R410a | R410a | R410a | R410a
30 |  | Charge | g | 830 | 990 | 1020 | 1300 | 2050 | 2300
Remark: The above design and specification are subject to change without prior notice for product improvement.
| Rating Conditions |  |  | Cooling | Heating
| Indoor Temperature |  |  | 27oC DB/19oC WB | 20oC DB/15oC WB
| water inlet temperature |  |  | 30oC | ----
| water outlet temperature |  |  | 35oC | ----