## fan coil
Technical Specification-Fan Coil Unit
Model |  |  |  | FP-34 | FP-51 | FP-68 | FP-85 | FP-102 | FP-1360 | FP-170 | FP-204 | FP-238
Air flow | m3/h | H |  | 340 | 510 | 680 | 850 | 1020 | 1360 | 1700 | 2040 | 2380
|  | M |  | 285 | 397.5 | 540 | 675 | 810 | 1229.25 | 1443.75 | 1782 | 1960.2
|  | L |  | 190 | 265 | 360 | 450 | 540 | 931.25 | 1093.75 | 1350 | 1512.5
Cooling Capacity | W | H |  | 1800 | 2700 | 3600 | 4500 | 5400 | 6585 | 7264 | 9323 | 10010
|  | M |  | 1620 | 2440 | 3290 | 4120 | 4850 | 5991 | 6938 | 8399 | 9200
|  | L |  | 1310 | 2010 | 2650 | 3320 | 3900 | 4847 | 5599 | 6785 | 7428
Heating Capacity | W | H |  | 2400 | 3510 | 4500 | 6160 | 7060 | 9420 | 11020 | 14740 | 16930
|  | M |  | 2040 | 3050.6667 | 3775 | 5512.0593 | 5970.4938 | 8076.7778 | 9583.3185 | 12865.6543 | 14654.7513
|  | L |  | 1780 | 2597.4 | 3330 | 4558.4 | 5083.2 | 6782.4 | 7934.4 | 10760.2 | 12020.3
Power Input | W | H | 12Pa | 37 | 52 | 62 | 76 | 96 | 134 | 152 | 189 | 228
|  | SH | 30Pa | 44 | 59 | 72 | 87 | 108 | 156 | 174 | 212 | 253
|  | SH | 50Pa | 49 | 66 | 84 | 100 | 118 | 174 | 210 | 250 | 300
Noise dB(A) | dB(A) | SH | 50Pa | 42 | 44 | 46 | 47 | 49 | 50 | 52 | 54 | 56
|  | SH | 30Pa | 40 | 42 | 44 | 46 | 47 | 48 | 50 | 52 | 54
|  | H | 12Pa | 37 | 39 | 41 | 43 | 45 | 46 | 48 | 50 | 52
|  | M |  | 30 | 32 | 34 | 36 | 38 | 39 | 40 | 42 | 43
|  | L |  | 24 | 25 | 27 | 28 | 29 | 30 | 31 | 32 | 33
Water Flow | L/h |  |  | 360 | 482 | 655 | 814 | 936 | 1285.2 | 1397.4 | 1768 | 1870
Water Pressure Drop | kPa |  |  | 20 | 20 | 20 | 30 | 40 | 40 | 40 | 40 | 50
Water in/out pipe |  | 3/4” FPT
Drain Pipe Size |  | 3/4” MPT
Note: 1.Testing condition: Cooling: entering air temp 27*C DB/19.5*C WB; entering water temp 7*C, leaving water temp 12*C; Heating: entering air temp 21*C; entering water temp 60*C, leaving water temp 55*C; 2.Sound pressure level are measured in acoustic room, position of the measure point is 1m in the front and 1m below the vertical center line of the unit 3.Static pressure is measured without filter and air outlet.