## 4R AHU
Technical Specification-Air Handling Unit
4 row parameter
Model AZAF | Normal air flow m3/h | Cooling capacity |  | Heating capacity |  | Water flow |  | Water resistance
|  | return air condition | fresh air condition | return air condition | fresh air condition | return air condition | fresh air condition | return air condition | fresh air condition
20 | 2000 | 10.72 | 18.94 | 15.58 | 25.315 | 1.95 | 3.25 | 16 | 31.8
30 | 3000 | 16.2 | 27.335 | 25.37 | 41.455 | 3 | 5.55 | 16.9 | 34
40 | 4000 | 22.68 | 41.565 | 32.255 | 53.56 | 3.9 | 7.15 | 17.2 | 35.6
50 | 5000 | 31.83 | 60.375 | 42.105 | 71.41 | 5.5 | 10.5 | 23 | 45
60 | 6000 | 35.39 | 61.605 | 47.14 | 81.635 | 6.15 | 10.7 | 27 | 50
70 | 7000 | 43.75 | 80.72 | 54.925 | 96.91 | 7.55 | 14 | 30.2 | 52
80 | 8000 | 48.8 | 88.255 | 64.525 | 108.74 | 8.45 | 15.285 | 32.9 | 54
100 | 10000 | 60.22 | 116.695 | 82.93 | 142.42 | 10.45 | 20.2 | 38.5 | 56
120 | 12000 | 76.42 | 145.695 | 102.825 | 175.1 | 13.25 | 25.25 | 43.1 | 60
150 | 15000 | 97.51 | 188.91 | 130.61 | 224.465 | 16.9 | 32.75 | 49.1 | 62
180 | 18000 | 121.99 | 235.075 | 161.825 | 277.245 | 21.1 | 40.7 | 52 | 64
200 | 20000 | 133.83 | 257.89 | 178.33 | 305.675 | 23.2 | 44.6 | 54 | 66
220 | 22000 | 146.88 | 281.34 | 196.065 | 334.885 | 25.4 | 48.65 | 55 | 66
250 | 25000 | 163.9 | 314.1 | 211.745 | 362.395 | 28.4 | 54.4 | 55 | 67
270 | 27000 | 170.32 | 322.865 | 251.705 | 407.64 | 28.1 | 55.9 | 32.9 | 54
300 | 30000 | 177.8 | 333.165 | 274.86 | 448.48 | 30.8 | 57.7 | 35.2 | 56
350 | 35000 | 217.68 | 420.18 | 306.36 | 518.06 | 37.7 | 72.7 | 39 | 60
400 | 40000 | 257.39 | 495.985 | 346.46 | 593.585 | 44.6 | 85.9 | 38.5 | 56
450 | 45000 | 288.58 | 547.215 | 388.415 | 659.195 | 50 | 94.75 | 43.1 | 60
500 | 50000 | 322.24 | 611.045 | 433.495 | 735.62 | 55.8 | 105.85 | 46 | 61
600 | 60000 | 390.86 | 723.18 | 524.265 | 898.415 | 67.7 | 130.45 | 49.1 | 62
800 | 80000 | 430 | 815 | 578 | 981 | 73.96 | 142 | 55 | 66
1000 | 100000 | 639 | 1184 | 858 | 1471 | 110 | 205 | 58 | 68

## 6R AUH
Technical Specification-Air Handling Unit
6 row parameter
Model AZAF | Normal air flow m3/h | Cooling capacity |  | Heating capacity |  | Water flow |  | Water resistance
|  | return air condition | fresh air condition | return air condition | fresh air condition | return air condition | fresh air condition | return air condition | fresh air condition
20 | 2000 | 14.15 | 26.745 | 19.35 | 33.095 | 2.45 | 4.65 | 21 | 36.8
30 | 3000 | 19.16 | 35.205 | 27.73 | 48.705 | 3.3 | 6.1 | 21.9 | 39
40 | 4000 | 29.46 | 54.13 | 39.535 | 66.545 | 5.1 | 9.4 | 22.2 | 40.6
50 | 5000 | 34.63 | 63.63 | 46.075 | 80.9 | 6 | 11 | 28 | 50
60 | 6000 | 41.14 | 74.675 | 56.88 | 98.4 | 7.1 | 12.95 | 32 | 55
70 | 7000 | 49.78 | 91.465 | 67.885 | 118.96 | 8.65 | 16.7 | 35.2 | 57
80 | 8000 | 58.96 | 108.34 | 79.075 | 138.475 | 10.25 | 18.75 | 37.9 | 59
100 | 10000 | 75.97 | 139.585 | 100.915 | 169.91 | 13.15 | 24.15 | 43.5 | 61
120 | 12000 | 94.43 | 173.515 | 124.15 | 94.04 | 16.35 | 30 | 48.1 | 65
150 | 15000 | 119.62 | 219.795 | 156.9 | 264.235 | 20.7 | 38 | 54.1 | 67
180 | 18000 | 138.98 | 255.485 | 175.275 | 307.14 | 24.1 | 44.2 | 57 | 69
200 | 20000 | 145.44 | 266.44 | 193.885 | 339.06 | 25.2 | 46.05 | 59 | 69
220 | 22000 | 156.28 | 287.175 | 213.225 | 373.575 | 27.1 | 49.65 | 60 | 69
250 | 25000 | 180.48 | 331.63 | 243.88 | 423.665 | 31.25 | 57.35 | 60 | 69
270 | 27000 | 198.47 | 393.035 | 266.67 | 477.46 | 34.35 | 65.7 | 37.9 | 59
300 | 30000 | 225.23 | 413.86 | 301.075 | 515.185 | 39 | 71.65 | 40.2 | 61
350 | 35000 | 271.01 | 497.965 | 358.735 | 613.6 | 46.9 | 86.2 | 44 | 65
400 | 40000 | 316.49 | 581.545 | 417.355 | 687.35 | 54.8 | 100.65 | 43.5 | 61
450 | 45000 | 355.34 | 652.315 | 468.11 | 800.33 | 61.55 | 112.9 | 48.1 | 65
500 | 50000 | 396.09 | 727.65 | 521.68 | 859.03 | 53.6 | 126 | 51 | 66
600 | 60000 | 478.71 | 878.325 | 630.145 | 1035.265 | 82.9 | 152.1 | 54.1 | 67
800 | 80000 | 502 | 921 | 660 | 1088 | 86 | 160 | 59 | 70
1000 | 100000 | 759 | 1394 | 1000 | 1643 | 130 | 240 | 60 | 70